Campus Safety Advisory Committee Annual Report – Academic Year 2025-2026

Meeting Dates: 11/06/2025, 11/25/2025, 4/07/2026

Committee Members:

Chief Daniel Daugherty

Coryn Voels

Debbie Nilsen

Dr. Jill Silverman

Dr. Brian Kelly

Justina Geremia

Dr. Deanna Devlin

Ashley Granger - student

Erin Looney – student

Aaron Solomon – student

Katherine Romano – Alumni Representative

Guest Presenters:

Ryan Kleinkopf - Fire Marshal

Frank Rampello - Asst. Dean of students

Michael Nembhard - Dean of Students

Lauren Umbrino - Resident Director

Introduction

This year’s Campus Safety Advisory Committee dealt with two significant safety issues for the FSC community.  The first was addressing East Farmingdale Fire Department’s response to FSC and the strains that false activations were having on their department’s ability to turnout for calls and overall department morale. The other was overseeing the installation of new automated external defibrillators (AEDs) on campus.

Fire department response to false alarm activations

More than 23 false fire alarms were recorded in residence halls between August 2025 and November 2025. Common causes included hair styling equipment, shower steam, and vaping. These incidents strained local fire department resources and campus operations. Through the Campus Fire Marshal, EFFD requested assistance in lowering the number of times it would be needed to respond to non-fires.  The Campus Safety Advisory Committee convened its second meeting and included representatives from Residence Life, the Dean of Students Office and the Campus Fire Marshal to discuss what could be done from the campus constituents.

RD Lauren Umbrino reported that resident students are aware of the frequent false alarms and practices that have produced many of them. RLO has begun an effort to remind students of how sensitive the systems are and encourage them to minimize behaviors that may unintentionally trigger alarms. The committee agreed with the potential value of an educational campaign to improve student awareness and reduce accidental activations.  Other educational efforts were discussed and will be developed by the Dean of Students office in conjunction with the Campus Fire Marshal.

Ryan Kleinkopf, the Campus Fire Marshal, worked with EFFD and University Police and created procedural changes to help alleviate the problem.  First off, the residence Hall fire alarm system was switched to a “Single head local activation.” This means that if an alarm is activated by a single smoke head, the alarms will sound for the entire suite but not the entire building. Suite occupants will immediately evacuate the suite to the building lobby and await University Police’s arrival. UPD will receive the alarm to its dispatch console and send officers. Meanwhile, EFFD will be notified of the single zone activation and be on standby.  UPD officers will respond and report to dispatch the conditions.  If a second smoke head is activated, or if UPD determines EFFD response is necessary, EFFD will be dispatched immediately. A second smoke head activation will also trigger the entire building to alarm and residents to evacuate. In cases of a single zone activation and EFFD is not needed to respond, UPD officers will reset the fire alarm and document the reason for the single zone activation.  All UPD officers were trained by the Fire Marshal in January on the new procedures. These new measures have already produced positive results as EFFD has not had to respond to multiple false activations.  UPD administration will continue to evaluate these procedures in order to maintain the safety of the campus community and the effectiveness of its emergency response.

Automated External Defibrillator Campus-wide Upgrade

A total of 80 brand new Cardiac Science AEDs have been placed around the entire campus, as well as the Aerospace facility and the Brentwood EOC building. These replace older ones that were fully functional but whose warranties were expiring. Additionally, the Fire Marshal will now be taking over the AED program and maintaining these devices. The monthly checks of these devices will be conducted in conjunction with his fire extinguisher checks and building inspections. Of course, UPD will assist in maintaining these devices as needed.

Conclusion

This year’s projects that the Campus Safety Advisory Committee undertook will go a long way to enhancing the safety and security of everyone at Farmingdale State College.  Additionally, it is very satisfying to see the level of cooperation between the various campus departments focused on a goal to help make FSC a safe campus for all individuals. The committee looks forward to continuing these efforts and taking on new ones in the upcoming academic year.